The MimicB60 board is an addressable synoptic system which can drive up to 60-LEDs.

The MimicB60 product is made of an electronic board mounted into a plastic socket compatible with OMEGA rail fixing.

The MimicB60 board is compatible with Héphaïs 1600 and Héphaïs 1600 NE. A maximum of 3 boards can be connected on a loop and each is declared by 60 addresses on the loop.

Main characteristics

- 60 addressable leds fully programmable

- Embedded isolator

- Rail DIN installation

- Led panels associated

| Electrical characteristics |  |  |
| --- | --- | --- |
| Communication bus voltage |  | Extreme: 12 to 28V Nominal: 24Vdc |
| Leds power supply |  | Extreme: 15 to 28V Nominal: 24Vdc |
| Standby consumption (under 24V) |  | 24mA |
| Initialisation duration (switch on) |  | <1.0 sec |
| Energy reserve (in case of power failure) |  | < 4 sec |
| Leds output, power |  | 17 W (60Leds) i.e 24V/12mA max per led |
| Leds output, type |  | Leds output in common anode |
| Short-circuit isolator |  |  |
| Max. current | - ISmax = 1.0 A in commutation - ICmax = 400mA in permanence (closed isolator) - ILmax = 100µA (open isolator) |  |
| Impedance (line switch) | < 400mΩ @ 400mA when closed - 100KΩ when opened |  |
| Switch opening voltage | 9 Vdc < Uline < 10Vdc |  |
| Fuse |  |  |
| Nominal current | 1.0A |  |
| Dimensions in mm (l x w) | 20 x 5 |  |
| Mechanical characteristics |  |  |
| Weight | 320 g (with female connectors) |  |
| Dimension in mm (l x w x h) | 206x109x60.5 |  |
| Protection index | IP00 (no protection) |  |
| Climatic characteristics |  |  |
| Operating mode Temperature | From -10°C to +60°C |  |
| Operating mode Humidity | ≤ 93% HR |  |
| Storage Temperature | From -10°C to +60°C |  |
| Storage Humidity | ≤ 93% HR |  |

REFERENCE	DESCRIPTION

MIMICB60	DIN RAIL MOUNTING 60 ADDRESSABLE outputs dedicated for Mimic panel leds